## BOQ & Estimate
BILL OF QUANTITIES & COST ESTIMATE
Underground CBRN-Hardened Ops Room (22.0 m × 6.2 m Box)
WORKS MANAGEMENT & SCHEDULE PARAMETERS
Total Duration | 224 Working Days
Scheduled Dates | 02-11-2026 to 26-07-2027
Working Week | 6 Days / Week
Monsoon Relaxation | 3 Days / Month
Milestone 1 | Substructure Finish (18-12-26)
Milestone 2 | Superstructure Finish (26-03-27)
Milestone 3 | Hand-Over (26-07-27)
Specifications | M35 RCC & Fe500D (Blast Governed)
1. CONCRETE ESTIMATE
# | Structural Component & Geometry | Grade | Quantity | Unit
1.1 | Bottom PCC Levelling Bed for Raft Mat (100 mm thk) | M15 | 17.17 | m³
1.2 | Monolithic Mat Raft Foundation (600 mm thk) | M35 | 81.84 | m³
1.3 | Perimeter External Shear Walls W1–W4 (600 mm thk) | M35 | 108.29 | m³
1.4 | Internal Structural / Blast Shaft Walls W5–W7 | M35 | 24.32 | m³
1.5 | Pressure Roof Slab (900 mm thk, deduct stair void) | M35 | 114.72 | m³
1.6 | Internal Dog-Leg Staircase Flights & Intermediate Landings | M35 | 4.8 | m³
1.7 | Internal Sump Pit (1.5 m³) & Equipment Plinth Pads | M35 | 6.4 | m³
1.8 | Entry Headhouse (400 mm Walls, 500 mm Roof Slab) | M35 | 28.56 | m³
1.9 | Approach Stairwell Box (250 mm Raking Wall & Roof) | M35 | 18.2 | m³
1.10 | Sacrificial RC Burster Slab in 2 m Soil Overburden (200 mm — RC1 R-1, was 300 mm) | M30 | 38.4 | m³
1.11 | Detached Sentry Post — RC FRAME ONLY (footings, plinth, columns, beams, slabs). Brick infill measured as brickwork — RC1 R-6 | M30 | 18.6 | m³
1.12 | Escape shaft collars ESC 1 and ESC 2, 250 RC, OD 1900 — ADDED BY RC1 R-7, missing from the bill | M35 | 6.285 | m³
| TOTAL CONCRETE QUANTITY (sum of the lines above — RC1 R-13) |  | 467.59 | m³
2. STEEL REINFORCEMENT ESTIMATE (Fe500D)
# | Bar Diameter & Structural Application | Net Weight (kg) | Wastage | Gross Weight (Tonnes)
2.1 | 8 mm Bars (Hoops, Ties, Sentry Post Reinforcement) | 1120 | 0.05 | 1.18
2.2 | 10 mm Bars (Distribution Steel & Secondary Links) | 1480 | 0.05 | 1.55
2.3 | 12 mm Bars (Shear Links, Burster Slab, Internal Partitions) | 9390 | 0.05 | 9.86
2.4 | 16 mm Bars (Perimeter Walls, Raft Foundation Mesh) | 24140 | 0.05 | 25.35
2.5 | 20 mm Bars (Shaft Walls W6/W7, Headhouse, Haunches) | 8740 | 0.05 | 9.18
2.6 | 25 mm Bars (Pressure Slab Main Curtains & Opening Trimmers) | 19690 | 0.05 | 20.67
| TOTAL REINFORCEMENT STEEL | 64560 |  | 67.79

## Detailed BOQ
Part | # | Item Description | Unit | Qty | Rate (₹) | Material (₹) | Labour Deployment | Total Cost (₹)
PART I - SURVEY, SITE CLEARANCE & EXCAVATION
PART I - SURVEY, SITE CLEARANCE & EXCAVATION | 1 | Confirmatory Soil & Rock Core Boreholes | No | 4 | 50000 | 200000 | 2 Trad / 4 Maz (10 d) | 234660
PART I - SURVEY, SITE CLEARANCE & EXCAVATION | 2 | Site Clearance, Grubbing & Setting Out | Sqm | 1800 | 44.8 | 80640 | 1 Trad / 6 Maz (4 d) | 96500
PART I - SURVEY, SITE CLEARANCE & EXCAVATION | 3 | Mass Excavation in Basalt / Murum (~6.8 m) | Cum | 1539 | 850 | 1308150 | 2 Trad / 10 Maz (30 d) | 1512570
PART I - SURVEY, SITE CLEARANCE & EXCAVATION | 4 | Surface Dressing & Anti-Termite Treatment | Sqm | 320 | 180 | 57600 | 1 Trad / 4 Maz (4 d) | 68996
[7 empty] | SUBTOTAL | 1912726
PART II - SUBSTRUCTURE & FOUNDATION WORKS
PART II - SUBSTRUCTURE & FOUNDATION WORKS | 1 | Formwork for Mat Raft & Bay 5 Sump | Sqm | 125 | 410 | 51250 | 4 Trad / 6 Maz (5 d) | 82750
PART II - SUBSTRUCTURE & FOUNDATION WORKS | 2 | PCC 1:3:6 Levelling Bed (100 mm) | Cum | 17.17 | 5500 | 94435 | 2 Trad / 8 Maz (2 d) | 105831
PART II - SUBSTRUCTURE & FOUNDATION WORKS | 3 | Monolithic Mat Raft Casting (M35) | Cum | 81.84 | 8640 | 707098 | 4 Trad / 12 Maz (6 d) | 762082
PART II - SUBSTRUCTURE & FOUNDATION WORKS | 4 | Pre-Applied Waterproofing Membrane + Screed | Sqm | 280 | 950 | 266000 | 2 Trad / 4 Maz (4 d) | 280832
PART II - SUBSTRUCTURE & FOUNDATION WORKS | 5 | Dual Swelling Hydrophilic Kicker Waterstops | M | 68 | 650 | 44200 | 2 Trad / 2 Maz (3 d) | 51976
[7 empty] | SUBTOTAL | 1283471
PART III - SUPERSTRUCTURE & STRUCTURAL RCC
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 1 | Formwork for 600 mm Shear Walls (3.2 m Ht) | Sqm | 480 | 580 | 278400 | 6 Trad / 12 Maz (12 d) | 411888
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 2 | Casting 600 mm Perimeter & Shear Walls (M35) | Cum | 132.61 | 8640 | 1145750 | 4 Trad / 16 Maz (8 d) | 1236918
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 3 | Formwork & Staging for 900 mm Pressure Slab | Sqm | 145 | 650 | 94250 | 6 Trad / 14 Maz (10 d) | 216650
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 4 | Casting 900 mm Pressure Roof Slab (M35) | Cum | 114.72 | 8640 | 991181 | 6 Trad / 18 Maz (6 d) | 1073657
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 5 | Internal Dog-Leg Staircase RCC | Cum | 4.8 | 9200 | 44160 | 2 Trad / 4 Maz (4 d) | 58992
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 6 | Headhouse Structure (400 mm Wall / 500 mm Roof) | Cum | 28.56 | 8640 | 246758 | 3 Trad / 6 Maz (6 d) | 280130
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 7 | Approach Stairwell RC Box (250 mm RC) | Cum | 18.2 | 8640 | 157248 | 2 Trad / 4 Maz (5 d) | 175788
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 8 | Engineered burster slab (200 mm M30 — RC1 R-1, was 300 mm M35). Rate carried from the owner's own bill; a grade change may warrant a rate review [REVIEW] | Cum | 38.4 | 8200 | 314880 | 3 Trad / 8 Maz (6 d) — scaled with the quantity | 340140
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 9 | Sentry post RC frame — brick infill measured as brickwork (RC1 R-6) | Cum | 18.6 | 8500 | 158100 | 2 Trad / 4 Maz (8 d) | 187764
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 10 | 110 mm Internal Brick Partition Walls | Sqm | 95 | 920 | 87400 | 2 Trad / 4 Maz (6 d) | 109648
PART III - SUPERSTRUCTURE & STRUCTURAL RCC | 11 | Escape shaft collars ESC 1 and ESC 2, 250 RC, OD 1900 — ADDED BY RC1 R-7 | Cum | 6.285 | 8640 | 54302 | [DATA REQUIRED — labour not priced here; no figure for it exists in the project and none is invented] | 54302
[7 empty] | SUBTOTAL | 4145877
PART IV - REINFORCEMENT STEEL & SHIELDING
PART IV - REINFORCEMENT STEEL & SHIELDING | 1 | Pressure Roof Slab Rebar (T25 / T12) | Tonne | 23.22 | 78000 | 1811160 | 6 Trad / 12 Maz (18 d) | 2011392
PART IV - REINFORCEMENT STEEL & SHIELDING | 2 | Perimeter & Shear Wall Rebar (T16 / T20) | Tonne | 17.85 | 78000 | 1392300 | 6 Trad / 12 Maz (16 d) | 1570284
PART IV - REINFORCEMENT STEEL & SHIELDING | 3 | Mat Raft & Haunch Diagonal Rebar | Tonne | 13.14 | 78000 | 1024920 | 5 Trad / 10 Maz (12 d) | 1136160
PART IV - REINFORCEMENT STEEL & SHIELDING | 4 | Headhouse, Approach & Staircase Steel | Tonne | 6.76 | 78000 | 527280 | 4 Trad / 8 Maz (10 d) | 601440
PART IV - REINFORCEMENT STEEL & SHIELDING | 5 | Burster Slab Mesh (T12 @ 150 B/W) [REVIEW — RC1 R-12: T12 @ 150 B/W is 11.84 kg/m2 whatever the slab thickness, so the R-1 thickness ruling does NOT change this line. The owner's tonnage over their own plan area implies about 15 kg/m2; that is a separate question and is NOT overwritten here] | Tonne | 2.89 | 78000 | 225420 | 3 Trad / 6 Maz (6 d) | 258792
PART IV - REINFORCEMENT STEEL & SHIELDING | 6 | Sentry Post Structural Rebar | Tonne | 3.93 | 78000 | 306540 | 2 Trad / 4 Maz (8 d) | 336204
PART IV - REINFORCEMENT STEEL & SHIELDING | 7 | EMP Welding at 4th Node & Bonding Straps | Item | 1 | 380000 | 380000 | 2 Trad / 2 Maz (15 d) | 418880
[7 empty] | SUBTOTAL | 6333152
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 1 | Blast Doors 1 & 2 (≥7 bar, Rebound-Rated) | Set | 2 | 1250000 | 2500000 | 4 Trad / 6 Maz (8 d) | 2550400
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 2 | Emergency Exit Hatches (900 mm Clear, 621 kPa) | Set | 2 | 450000 | 900000 | 2 Trad / 4 Maz (6 d) | 922248
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 3 | Fast-Acting Blast Valves BV-1 to BV-3 (DN100) | Set | 3 | 160000 | 480000 | 2 Trad / 2 Maz (4 d) | 490368
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 4 | Generator Blast Valves BV-4 & BV-5 (DN350) | Set | 2 | 320000 | 640000 | 2 Trad / 2 Maz (4 d) | 650368
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 5 | NBC Collective Protection Trains (2 × 300 m³/h) | Set | 2 | 1850000 | 3700000 | 4 Trad / 4 Maz (14 d) | 3772576
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 6 | Sealed Zone-2 Welded EMP Enclosure (3×3×2.4 m) | Item | 1 | 850000 | 850000 | 2 Trad / 4 Maz (12 d) | 894496
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 7 | Layerwise Engineered Fill & Basalt Rubble Berm | Cum | 620 | 420 | 260400 | 2 Trad / 10 Maz (12 d) | 342168
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 8 | Submersible Sump Pumps + Effluent Piping + Septic | Set | 1 | 420000 | 420000 | 2 Trad / 4 Maz (10 d) | 456500
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 9 | Sand-Faced Internal Plaster, Punning & Painting | Sqm | 720 | 180 | 129600 | 4 Trad / 6 Maz (12 d) | 199632
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 10 | Testing, Commissioning & Envelope Leakage Test | Item | 1 | 250000 | 250000 | 4 Trad / 2 Maz (4 d) | 266272
[7 empty] | SUBTOTAL | 10545028
PART V - CBRN, EMP, CLOSURES & ANCILLARY SERVICES | 11 | Standby generator 15 kVA in Bay 8, with fuel system, exhaust and acoustic treatment — ADDED BY RC1 R-8. The bill prices the 2 600 m3/h combustion and cooling air path through BV-4/BV-5 but not the machine | Set | 1 | [DATA REQUIRED — vendor quotation. NO RATE IS INVENTED] | 0 | [DATA REQUIRED] | 0

## Cost Summary
Cost Head Component | Basis / % Addition | Cost Incurred (₹)
Total Basic Cost | Subtotal Packages | 24220254
Contingencies | 3.0% | 726608
Water & Electricity Provisions | 1.0% | 242203
Specialist CBRN / EMP & Engineering Consultant | 6.0% | 1453215
Site Supervision & Quality Assurance | 2.0% | 484405
Statutory Clearances & Liaisoning | 1.0% | 242203
Contractor's Overhead & Profit | 10.0% | 2422025
FINAL PROJECT COST | - | 29790913